## OTPs Standard URP(-AS)_EXAMPLE
**COLUMN INCLUDED IN ACTUAL URP (-AS) .CSV FILE** | **COLUMN INCLUDED IN ACTUAL URP (-AS) .CSV FILE** | **UNITS ADD TO GIVE CONTEXT** | **DETAILS THE REQUIRED FIELDS** | **EXPLAINS FILE TYPE** | **NOTES TO PROVIDE ADDITIONAL CONTEXT**
Color Coding: | Required Fields To Be Filled In By DER System Installer
PARAMETER | VALUE | Units | Required Field | Units | Notes
COMMENT | THIS FILE IS THE APPLIED SETTINGS OR -AS FILE FOR THE INSTALLATION
MT_FILE_INFO_TYPE | AS |  |  |  | Context of the data in the file - SS is the utility specified settings file -AS is the returned As Set file
COMMENT | BASIC_INVERTER_INFORMATION
NP_P_MAX | 1000 | W | Required | Number | Active power rating in watts at unity power factor
NP_P_MAX_OVER_PF |  | W |  | Number | Active power rating in watts at specified over-excited power factor
NP_OVER_PF |  |  |  | Number | Over-excited power factor (VArs injected)
NP_P_MAX_UNDER_PF |  | W |  | Number | Active power rating in watts at specified under-excited power factor
NP_UNDER_PF |  |  |  | Number | Under-excited power factor (VArs absorbed)
NP_VA_MAX | 1000 | VA | Required | Number | Maximum apparent power rating in volt-amperes
NP_NORMAL_OP_CAT | CAT_B |  | Required | Selection List | Normal operating performance category
NP_ABNORMAL_OP_CAT | CAT_III |  | Required | Selection List | Abnormal operating performance category
NP_Q_MAX_INJ |  |  |  | Number | Maximum injected reactive power rating in volt-amperes reactive
NP_Q_MAX_ABS |  |  |  | Number | Maximum absorbed reactive power rating in volt-amperes reactive
NP_P_MAX_CHARGE |  |  |  | Number | Maximum active power charge rating in watts
NP_APPARENT_POWER_ CHARGE_MAX |  |  |  | Number | Maximum apparent power charge rating in volt-amperes. May differ from the apparent power maximum rating
NP_AC_V_NOM-SS | 240 | V | Required | Number | Base nominal AC voltage rating in RMS Vac
NP_AC_V_MAX |  |  |  | Number | Maximum output RMS AC voltage (VH) in the continuous operating region
NP_AC_V_MIN |  |  |  | Number | Minimum output RMS AC voltage (VL) in the continuous operating region
NP_SUPPORTED_MODES | QV-QP-PV-CONST_PF-CONST_Q-PF |  | Required | Mulit-List | Indication of support for each control mode function separated by dashes
NP_REACTIVE_SUSCEPTANCE |  |  |  | Number | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state
NP_MANUFACTURER | Enphase |  | Required | Text | Manufacturer
NP_MODEL | IQ8PLUS |  | Required | Text | Model
NP_SERIAL_NUM | IQ8SP-12A-DSH-00207-2.0-EN-US-2023-10-13 |  | Required | Text | Serial number
NP_FW_VER | 2.48.01 |  | Required | Text | Firmware version
AP_LIMIT_ ENABLE | DISABLED |  | Required | P p.u | Limit active power function ENABLED or DISABLED
AP_LIMIT | 0 |  | Required | Number | Active power limit setting. Per unit value based on NP_P_MAX or NP_P_MAX_CHARGE. Negative values indicate active power absorption
COMMENT | ENTER_ SERVICE_PARAMETERS (1547 Defaults)
ES_PERMIT_SERVICE-AS | ENABLED |  | Required | Selection List | Permit service function enable. This function is activated by request from the Area EPS Operator
ES_V_LOW-AS | 0.917 | V p.u. | Required | Number | Enter service voltage - low - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_V_HIGH-AS | 1.05 | V p.u. | Required | Number | Enter service voltage - high - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_F_LOW-AS | 59.5 | Hz | Required | Number | Frequency in Hz, and shall be reported to 3 decimal places
ES_F_HIGH-AS | 60.1 | Hz | Required | Number | Frequency in Hz, and shall be reported to 3 decimal places.
ES_DELAY-AS | 300 | Seconds | Required | Number | Minimum intentional enter service delay
ES_RANDOMIZED_DELAY-AS | 300 | Seconds | Required | Number | Enter service randomized delay (optional feature in IEEE Std 1547-2018)
ES_RAMP_RATE-AS | 300 | Seconds | Required | Number | Enter service soft-start duration in seconds. Time from zero to 100% of NP_P_MAX.
COMMENT | CONSTANT_POWER_FACTOR_MODE_ PARAMETERS
CONST_PF_MODE_ENABLE-AS | DISABLED |  | Required | Selection List | Constant power factor mode enable
CONST_PF_EXCITATION-AS |  |  |  | Selection List | Under or over excited
CONST_PF-AS | 0.98 | PF |  | Number | Constant power factor setting, no sign should be used
CONST_Q_MODE_ENABLE-AS | DISABLED |  |  | Selection List | Constant reactive power mode select
CONST_Q-AS |  | Var p.u |  | Number | Injecting reactive power setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-VAR_MODE_PARAMETERS (1547 STANDARD VALUES)
QV_MODE_ENABLE-AS | ENABLED |  | Required | Selection List | Voltage-Reactive power mode enable.
QV_VREF-AS | 1 | V p.u. | Required | Number | Per unit value based on NP_AC_V_NOM (voltage base)
QV_VREF_AUTO_MODE-AS | DISABLED |  | Required | Selection List | Autonomous Vref adjustment enable.
QV_VREF_TIME-AS | 5 | Seconds | Required | Number | Vref adjustment time constant in seconds as specified by the area EPS operator
QV_CURVE_V1-AS | 0.92 | V p.u. | Required | Number | Volt-VAr point V1 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q1-AS | 0.44 | Var p.u | Required | Number | VArs at V1 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V2-AS | 0.98 | V p.u. | Required | Number | Volt-VAr point V2 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q2-AS | 0 | Var p.u | Required | Number | VArs at V2 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V3-AS | 1.02 | V p.u. | Required | Number | Volt-VAr point V3 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q3-AS | 0 | Var p.u | Required | Number | VArs at V3 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V4-AS | 1.08 | V p.u. | Required | Number | Volt-VAr point V4 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q4-AS | -0.44 | Var p.u | Required | Number | VArs at V4 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_OLRT-AS | 5 | Seconds | Required | Number | Volt-VAr open-loop response time
COMMENT | WATT-VAR_CONTROL_PARAMETERS
QP_MODE_ENABLE-AS | DISABLED |  | Required | Selection List | Active power-Reactive power mode enable
QP_CURVE_P3_GEN-AS |  | P p.u |  | Number | Watt-VAr point P3 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P2_GEN-AS |  | P p.u |  | Number | Watt-VAr point P2 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_GEN-AS |  | P p.u |  | Number | Watt-VAr point P1 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P1 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P2_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P2 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P3_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P3 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_Q3_GEN-AS |  | Var p.u |  | Number | VArs at point P3 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_GEN-AS |  | Var p.u |  | Number | VArs at point P2 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_GEN-AS |  | Var p.u |  | Number | VArs at point P1 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_LOAD-AS |  | Var p.u |  | Number | VArs at point P1 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_LOAD-AS |  | Var p.u |  | Number | VArs at point P2 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q3_LOAD-AS |  | Var p.u |  | Number | VArs at point P3 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-WATT_CONTROL_PARAMETERS (1547 STANDARD VALUES)
PV_MODE_ENABLE-AS | ENABLED |  | Required | Selection List | Voltage-Active power mode enable
PV_CURVE_V1-AS | 1.06 | V p.u. | Required | Number | Volt-Watt point V1 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P1-AS | 100 | V p.u. | Required | Number | Watts at point V1 setting. Per unit value based on NP_P_MAX.
PV_CURVE_V2-AS | 1.1 | V p.u. | Required | Number | Volt-Watt point V2 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P2-AS | 0 | V p.u. | Required | Number | Watts at point V2 setting. Per unit value based on NP_P_MAX or NP_P_MAX_CHARGE. Negative values indicate active power absorption.
PV_OLRT-AS | 10 | V p.u. | Required | Number | Volt-Watt - Open loop response time
COMMENT | OVER_UNDER_VOLTAGE_MUST_TRIP_PARAMETERS (MISO RECOMMENDED VALUES)
OV2_TRIP_V-AS | 1.2 | V p.u. | Required | Number | OV2 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV2_TRIP_T-AS | 0.16 | Seconds | Required | Number | OV2 must trip duration setting
OV1_TRIP_V-AS | 1.1 | V p.u. | Required | Number | OV1 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV1_TRIP_T-AS | 2 | Seconds | Required | Number | OV1 must trip duration setting
UV1_TRIP_V-AS | 0.7 | V p.u. | Required | Number | UV1 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV1_TRIP_T-AS | 5 | Seconds | Required | Number | UV1 must trip duration setting
UV2_TRIP_V-AS | 0.45 | V p.u. | Required | Number | UV2 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV2_TRIP_T-AS | 0.32 | Seconds | Required | Number | UV2 must trip duration setting
COMMENT | OVER_UNDER_FREQUENCY_MUST_TRIP_PARAMETERS (MISO RECOMENDED VALUES)
OF2_TRIP_F-AS | 62 | Hz | Required | Number | OF2 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF2_TRIP_T-AS | 0.16 | Seconds | Required | Number | OF2 must trip duration setting
OF1_TRIP_F-AS | 61.2 | Hz | Required | Number | OF1 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF1_TRIP_T-AS | 300 | Seconds | Required | Number | OF1 must trip duration setting
UF1_TRIP_F-AS | 58.5 | Hz | Required | Number | UF1 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF1_TRIP_T-AS | 300 | Seconds | Required | Number | UF1 must trip duration setting
UF2_TRIP_F-AS | 56.5 | Hz | Required | Number | UF2 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF2_TRIP_T-AS | 0.16 | Seconds | Required | Number | UF2 must trip duration setting
PF_DBOF-AS | 0.036 | Hz | Required | Number | Over frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_DBUF-AS | 0.036 | Hz | Required | Number | Under frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_KOF-AS | 0.05 | Number | Required | Number | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_KUF-AS | 0.05 | Number | Required | Number | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_OLRT-AS | 5 | Seconds | Required | Number | Frequency-Active power open-loop response time